BILL NO. 20 - 2014

ORDINANCE NO. _________

AN ORDINANCE OF THE CITY OF BETHLEHEM, COUNTIES

OF LEHIGH AND NORTHAMPTON, COMMONWEALTH OF PENNSYLVANIA, AMENDING ARTICLE 1701 OF THE

CODIFIED ORDINANCES ENTITLED PENNSYLVANIA UNIFORM

CONSTRUCTION CODE.

THE COUNCIL OF THE CITY OF BETHLEHEM HEREBY ORDAINS AS FOLLOWS:

SECTION 1.  That Section 1701.02 of the Codified Ordinances of the City of Bethlehem, entitled “Additions and Modifications”, which includes amendments to the International Building Code, is hereby amended to add the following:

IBC 903.4.2:  Alarms.  Approved audible devices shall be connected to every automatic sprinkler system.  Such sprinkler waterflow alarm devices shall be activated by waterflow equivalent to the flow of a single sprinkler of the smallest orifice size installed in the system.  Alarm devices shall be provided on the exterior of the building in an approved location.  Where a fire alarm system is installed, actuation of the automatic sprinkler system shall actuate the building fire alarm system.  In automatic sprinkler systems where multiple sprinkler risers are required, and the risers are located in separate areas within the building, an outside visible alarm notification appliance shall be required for each riser. Such appliance shall be a white strobe (minimum 95 candela strobe rating) placed in an approved location on the exterior wall, as close as practicable, to each sprinkler riser.  The strobe will activate when the water flow alarm for its respective riser is activated.

SECTION 2.  All Ordinances and parts of Ordinances inconsistent herewith be, and the same are hereby repealed.

Sponsored by	____________________________________

____________________________________

PASSED finally in Council on the          day of                                , 2014.

President of Council

ATTEST:

City Clerk

This Ordinance approved this            day of                                 , 2014.

Mayor